## San Juan Planes
plant | record_date | record_time | record_time_24h | operator | flow_lps | turbidity_raw_ntu | turbidity_clarified_ntu | turbidity_filtered_ntu | coag_num_hoses | coag_slider_pct | coag_dose_pct_mgl | coag_dose_probeta_mgl | coag_tank_vol_l | chlorine_slider_pct | chlorine_dose_pct_mgl | chlorine_dose_probeta_mgl | chlorine_tank_vol_l | has_flocs | purge | source_image | needs_review | review_notes
San Juan Planes | 2025-07-26 | 7 | 07:00 | Silvia | 11 | 2.02 | 0.31 |  | 3 | 12 | 2.12 | 5.45 | 210 | 28 | 0.5 | 0.5 | 90 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X' (no reading)
San Juan Planes | 2025-07-26 | 8:00 | 08:00 | Jose | 11 | 1.52 | 4.45 | 2.58 | 7 | 36 | 6.37 | 16 | 190 | 30 | 0.6 | 0.3 | 60 |  |  | 20260107_143129.jpg | TRUE | coag block values very unclear
San Juan Planes | 2025-07-26 | 8:30 | 08:30 | Jose | 11 | 2.47 | 0.36 |  | 7 | 62 | 1.09 | 28 | 190 | 30 | 0.6 | 0.3 | 60 |  |  | 20260107_143129.jpg | TRUE | coag block values very unclear
San Juan Planes | 2025-07-26 | 9 | 09:00 | Silvia | 10.5 | 1.46 | 0.4 |  | 3 | 10 | 1.77 | 4.95 | 200 | 30 | 0.6 | 0.5 | 80 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X'
San Juan Planes | 2025-07-26 | 9:00 | 09:00 | Jose | 11 | 1.27 | 1.44 | 0.1 | 7 | 30 | 5.36 | 14 | 196 | 36 | 0.6 | 0.3 | 60 |  |  | 20260107_143129.jpg | TRUE | coag block values unclear
San Juan Planes | 2025-07-26 | 11 | 11:00 | Silvia | 10.5 | 1.91 | 0.89 |  | 3 | 10 | 1.77 | 4.57 | 195 | 30 | 0.6 | 0.4 | 70 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X'
San Juan Planes | 2025-07-26 | 11:00 | 11:00 | Jose | 11 | 7.34 | 0.82 | 0.09 | 3 | 30 | 5.31 | 13 | 190 | 30 | 0.6 | 0.3 | 60 |  |  | 20260107_143129.jpg | TRUE | coag block unclear
San Juan Planes | 2025-07-26 | 1:30 | 13:30 | Silvia | 10.5 | 1.53 | 0.3 |  | 3 | 10 | 1.77 | 4.95 | 190 | 30 | 0.6 | 0.4 | 65 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X'
San Juan Planes | 2025-07-26 | 3:30 | 15:30 | Silvia | 12 | 10.61 | 0.63 |  | 3 | 10 | 1.77 | 4.33 | 185 | 30 | 0.6 | 0.4 | 60 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X'; raw unclear
San Juan Planes | 2025-07-26 | 5:20 | 17:20 | Silvia | 11 | 2.04 | 0.96 |  | 7 | 10 | 1.77 | 5.45 | 180 | 30 | 0.6 | 0.4 | 60 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X'
San Juan Planes | 2025-07-27 | 8:30 | 08:30 | Merlin | 11 | 5.51 | 0.54 | 0.01 | 3 | 12 | 2.12 | 4.36 | 130 | 45 | 0.6 | 0.3 | 50 |  |  | 20260107_143129.jpg | FALSE
San Juan Planes | 2025-07-27 | 10:30 | 10:30 | Merlin | 11 | 4.95 | 0.86 | 0 | 3 | 12 | 2.4 | 4.36 | 145 | 45 | 0.6 | 0.3 | 45 |  |  | 20260107_143129.jpg | FALSE
San Juan Planes | 2025-07-27 | 1:00 | 13:00 | Merlin | 11 | 4.94 | 0.86 | 0 | 3 | 12 | 2.4 | 4.35 | 146 | 45 | 0.6 | 0.3 | 45 |  |  | 20260107_143129.jpg | FALSE
San Juan Planes | 2025-07-27 | 2:00 | 14:00 | Jose | 11 | 4.88 | 0.69 | 0 | 3 | 30 | 5.31 | 9.4 | 150 | 30 | 0.8 | 0.2 | 50 |  |  | 20260107_143129.jpg | TRUE | coag block unclear
San Juan Planes | 2025-07-27 | 4:00 | 16:00 | Jose | 11 | 5.35 | 0.93 | 0 | 3 | 16 | 2.83 | 7.27 | 150 | 45 | 0.9 | 0.3 | 50 |  |  | 20260107_143129.jpg | FALSE
San Juan Planes | 2025-07-27 | 4:00 | 16:00 | Merlin | 11 | 5.61 | 1.51 | 1.03 | 3 | 12 | 2.4 | 4.35 | 149 | 45 | 0.6 | 0.3 | 45 |  |  | 20260107_143129.jpg | FALSE
San Juan Planes | 2025-07-27 | 5:30 | 17:30 | Jose | 11 | 4.5 | 0.77 | 0 | 3 | 12 | 2.12 | 5.45 | 150 | 56 | 0.1 | 0.3 | 50 |  |  | 20260107_143129.jpg | FALSE
San Juan Planes | 2025-07-29 | 7am | 07:00 | Silvia | 11.5 | 3.98 | 0.28 | 0.64 | 3 | 10 | 3.77 | 4.17 | 350 | 40 | 0.8 | 0.4 | 130 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-29 | 7:00 | 07:00 | Jose | 10.5 | 1.96 | 1.1 | 0.01 | 7 | 6 | 2.46 | 2.46 | 360 | 25 | 0.5 | 0.5 | 100 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | TRUE | coag block partly unclear
San Juan Planes | 2025-07-29 | 9am | 09:00 | Silvia | 11 | 3.62 | 0.46 | 0.44 | 3 | 10 | 1.77 | 4.36 | 340 | 40 | 0.8 | 0.4 | 125 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-29 | 9:00 | 09:00 | Jose | 10.5 | 2.68 | 1.69 | 0 | 7 | 8 | 3.28 | 3.28 | 360 | 28 | 0.56 | 0.5 | 100 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-29 | 11 | 11:00 | Silvia | 11 | 2.72 | 0.94 | 0.11 | 7 | 6 | 1.06 | 2.46 | 335 | 25 | 0.5 | 0.6 | 120 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-29 | 12:00 | 12:00 | Jose | 10.5 | 3.05 | 0.86 | 0 | 7 | 7 | 2.87 | 2.87 | 360 | 28 | 0.56 | 0.5 | 100 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-29 | 1:30 | 13:30 | Silvia | 11 | 2.78 | 0.99 | 0.11 | 7 | 6 | 1.06 | 2.46 | 330 | 25 | 0.5 | 0.5 | 110 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-29 | 3:30 | 15:30 | Silvia | 11 | 2.28 | 1.22 | 0.19 | 7 | 6 | 1.06 | 2.46 | 320 | 25 | 0.5 | 0.5 | 105 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-29 | 5:10 | 17:10 | Silvia | 10.5 | 3.18 | 2.62 | 0.19 | 7 | 6 | 1.06 | 2.46 | 330 | 25 | 0.5 | 0.6 | 100 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-30 | 7:30 | 07:30 | Merlin | 10 | 2.35 | 0.76 | 0 | 7 | 7 | 2.89 | 2.9 | 380 | 30 | 0.66 | 0.6 | 45 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-30 | 8am | 08:00 | Rosa | 11 | 1.43 | 0.89 | 0.01 | 7 | 7 | 2.87 | 2.9 | 380 | 30 | 0.66 | 0.6 | 60 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-30 | 11am | 11:00 | Rosa | 11 | 1.68 | 0.93 | 0.01 | 7 | 7 | 2.87 | 2.9 | 380 | 30 | 0.66 | 0.6 | 55 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-30 | 2:00 | 14:00 | Jose | 10.5 | 2.81 | 0.81 | 0 | 7 | 7 | 2.87 | 2.87 | 360 | 28 | 0.56 | 0.5 | 80 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-30 | 2pm | 14:00 | Rosa | 11 | 1.48 | 0.84 | 0 | 7 | 7 | 2.87 | 2.9 | 380 | 30 | 0.66 | 0.6 | 50 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-30 | 4:00 | 16:00 | Jose | 10.5 | 1.5 | 0.91 | 0 | 7 | 7 | 2.87 | 2.87 | 360 | 28 | 0.56 | 0.5 | 80 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-30 | 5pm | 17:00 | Rosa | 10 | 1.76 | 0.89 | 0.01 | 7 | 7 | 2.87 | 2.9 | 380 | 30 | 0.66 | 0.6 | 50 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-30 | 5:30 | 17:30 | Jose | 10.5 | 2.59 | 0.51 | 0 | 7 | 7 | 2.87 | 2.87 | 360 | 36 | 0.6 | 0.6 | 70 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | FALSE
San Juan Planes | 2025-07-30 | 10pm | 22:00 | Merlin | 10 | 1.35 | 0.1 | 0 | 7 | 7 | 2.87 | 2.9 | 380 | 30 | 0.66 | 0.6 | 44 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-07-31 | 1am | 01:00 | Merlin | 10 | 1.32 | 0.01 | 0 | 7 | 7 | 2.87 | 2.9 | 380 | 30 | 0.66 | 0.6 | 43 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-07-31 | 3am | 03:00 | Merlin | 10 | 1.32 | 0.01 | 0 | 7 | 7 | 2.87 | 2.9 | 380 | 30 | 0.66 | 0.6 | 42 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-07-31 | 7am | 07:00 | Hildeen | 10.5 | 1.89 | 0.41 | 0 | 7 | 7 | 2.87 | 2.85 | 400 | 30 | 0.6 | 0.6 | 100 |  |  | 20260107_143113.jpg | TRUE | operator name spelling
San Juan Planes | 2025-07-31 | 9am | 09:00 | Hildeen | 10.5 | 1.73 | 0.76 | 0 | 7 | 7 | 2.87 | 2.85 | 400 | 30 | 0.6 | 0.4 | 90 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-07-31 | 11am | 11:00 | Hildeen | 10.5 | 1.33 | 0.7 | 0 | 7 | 7 | 2.87 | 2.85 | 399 | 30 | 0.6 | 0.5 | 80 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-07-31 | 1pm | 13:00 | Hildeen | 10 | 1.93 | 0.22 | 0 | 7 | 7 | 2.87 | 3.6 | 398 | 30 | 0.6 | 0.5 | 70 |  |  | 20260107_143113.jpg | TRUE | coag probeta 3.6?
San Juan Planes | 2025-07-31 | 3pm | 15:00 | Hildeen | 10 | 1.22 | 0.91 | 0 | 7 | 7 | 2.87 | 2.85 | 398 | 30 | 0.6 | 0.6 | 70 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-07-31 | 5pm | 17:00 | Hildeen | 10 | 3.26 | 1.96 | 0.01 | 7 | 7 | 2.87 | 2.85 | 399 | 30 | 0.6 | 0.6 | 70 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-07-31 | 5:30 | 17:30 | Merlin | 10 | 1.31 | 0.01 | 0 | 7 | 7 | 2.87 | 2.9 | 380 | 30 | 0.66 | 0.6 | 40 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-07-31 | 7pm | 19:00 | Victor | 10.5 | 2.04 | 1.05 | 0 | 7 | 7 | 2.87 |  | 420 | 30 | 0.6 | 0.6 | 70 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-07-31 | 9pm | 21:00 | Victor | 10 | 1.26 | 0.97 | 0 | 7 | 7 | 2.87 |  | 420 | 30 | 0.6 | 0.5 | 60 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-07-31 | 11pm | 23:00 | Victor | 10.5 | 1.19 | 1.23 | 0.02 | 7 | 7 | 2.87 |  | 420 | 30 | 0.6 | 0.5 | 60 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-08-01 | 1am | 01:00 | Victor | 10 | 0.79 | 0.87 | 0.07 | 7 | 7 | 2.87 |  | 420 | 30 | 0.6 | 0.5 | 50 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-08-01 | 5am | 05:00 | Victor | 10 | 1.21 | 0.55 | 0 | 7 | 7 | 2.87 |  | 420 | 30 | 0.6 | 0.3 | 50 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-08-01 | 7:00 | 07:00 | Jose | 10 | 1.37 | 0.57 | 0 | 7 | 7 | 2.87 | 2.87 | 420 | 30 | 0.6 | 0.4 | 40 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-08-01 | 9:00 | 09:00 | Jose | 10 | 1.87 | 1.4 | 0 | 7 | 7 | 2.87 | 2.87 | 420 | 50 | 0.1 | 0.5 | 40 |  |  | 20260107_143113.jpg | FALSE
San Juan Planes | 2025-08-01 | 11:00 | 11:00 | Jose | 10.5 | 2.53 | 0.66 | 0 | 7 | 7 | 2.87 | 2.87 | 420 | 50 | 0.1 | 0.4 | 36 |  |  | 20260107_143104.jpg | TRUE | coag probeta overwritten
San Juan Planes | 2025-08-01 | 11 | 11:00 | Silvia | 10 | 0.76 | 0.97 | 0 | 7 | 6 | 2.46 | 2.46 | 420 | 60 | 1.2 | 0.4 | 10 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-01 | 3:20 | 15:20 | Jose | 10 | 2.68 | 1.45 | 0 | 8 | 8 | 3.28 | 3.28 | 420 | 50 | 0.1 | 0.4 | 36 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-01 | 5:00 | 17:00 | Jose | 10 | 1.77 | 1.28 | 0 | 8 | 8 | 3.28 | 3.28 | 420 | 60 | 1.2 | 0.5 | 20 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-01 | 7pm | 19:00 | Silvia | 10 | 1.14 | 0.76 | 0 | 7 | 8 | 3.28 | 3.28 | 430 | 60 | 1.2 | 0.4 | 30 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-01 | 9pm | 21:00 | Silvia | 10 | 2.18 | 1.86 | 0 | 7 | 6 | 2.46 | 2.46 | 425 | 60 | 1.2 | 0.4 | 20 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-02 | 7am | 07:00 | Victor | 10 | 1.1 | 0.39 | 0 | 7 | 6 | 2.46 |  | 420 | 15 | 0.3 | 0.6 | 151 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-02 | 9am | 09:00 | Victor | 10 | 1.01 | 0.7 | 0 | 7 | 6 | 2.46 |  | 420 | 15 | 0.3 | 0.4 | 148 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-02 | 11am | 11:00 | Victor | 11 | 1.03 | 0.88 | 0 | 7 | 6 | 2.46 |  | 420 | 15 | 0.3 | 0.4 | 148 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-02 | 1 | 13:00 | Silvia | 11 | 0.81 | 0.6 | 0 | 7 | 6 | 2.46 | 2.46 | 420 | 60 | 1.2 | 0.4 | 180 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-02 | 1pm | 13:00 | Victor | 11 | 0.65 | 0.72 | 0 | 7 | 6 | 2.46 |  | 420 | 25 | 0.5 | 0.4 | 148 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-02 | 3 | 15:00 | Silvia | 11 | 1.07 | 0.82 | 0 | 7 | 6 | 2.46 | 2.46 | 415 | 60 | 1.2 | 0.4 | 175 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-02 | 3pm | 15:00 | Victor | 11 | 1.11 | 1.23 | 0 | 7 | 6 | 2.46 |  | 420 | 25 | 0.5 | 0.3 | 148 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-02 | 5pm | 17:00 | Victor | 11 | 1.12 | 1.1 | 0.26 | 7 | 6 | 2.46 |  | 420 | 25 | 0.5 | 0.3 | 148 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-08-02 | 5:30 | 17:30 | Silvia | 11 | 2.53 | 1.02 | 0 | 7 | 6 | 2.46 | 2.46 | 420 | 60 | 1.2 | 0.4 | 170 |  |  | 20260107_143104.jpg | FALSE
San Juan Planes | 2025-12-09 | 1am | 01:00 | Victor | 12 | 6.8 | 0.5 | 0.29 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-09 | 5am | 05:00 | Victor | 12 | 2.19 | 0.86 | 0.39 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-09 | 7pm | 19:00 | Victor | 12 | 4.92 | 0.65 | 0.46 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-09 | 9pm | 21:00 | Victor | 12 | 6.92 | 0.52 | 0.74 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | TRUE | turbidity_raw_ntu 6.92?
San Juan Planes | 2025-12-09 | 11pm | 23:00 | Victor | 12 | 5.95 | 0.85 | 0.36 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-10 | 7:00 | 07:00 | Tulio | 12 | 8.9 | 0.97 | 0.68 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-10 | 7:00 | 07:00 | Jose | 12 | 6.17 | 0.85 | 0.58 |  | 10 | 4.1 | 4.66 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142313.jpg | TRUE | chlorine_dose_probeta unclear
San Juan Planes | 2025-12-10 | 9:00 | 09:00 | Tulio | 12 | 8.73 | 0.86 | 0.88 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-10 | 9:00 | 09:00 | Jose | 12 | 7.36 | 0.49 | 0.56 |  | 10 | 4.1 | 4.66 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-10 | 11:00 | 11:00 | Tulio | 12 | 4.52 | 0.94 | 0.81 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-10 | 11:00 | 11:00 | Jose | 12 | 8.08 | 1.03 | 0.66 |  | 10 | 4.1 | 4.66 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-10 | 1:00 | 13:00 | Tulio | 12 | 4.92 | 0.81 | 0.71 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-10 | 3:00 | 15:00 | Tulio | 12 | 6.7 | 0.96 | 0.63 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-10 | 5:00 | 17:00 | Tulio | 12 | 8.55 | 0.95 | 0.94 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-11 | 7am | 07:00 | Victor | 12 | 8.08 | 1.72 | 0.57 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-11 | 9am | 09:00 | Victor | 12 | 7.57 | 0.88 | 0.75 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-11 | 11am | 11:00 | Victor | 12 | 7.93 | 1.84 | 0.24 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-11 | 1:00 | 13:00 | Jose | 12 | 7.63 | 0.94 | 0.55 |  | 10 | 4.1 | 4.66 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-11 | 1pm | 13:00 | Victor | 12 | 7.93 | 1.3 | 0.57 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-11 | 3:00 | 15:00 | Jose | 12 | 8.86 | 0.76 | 0.78 |  | 10 | 4.1 | 4.66 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142313.jpg | TRUE | turbidity_clarified unclear
San Juan Planes | 2025-12-11 | 3pm | 15:00 | Victor | 12 | 5.04 | 1.02 | 0.75 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-11 | 5:00 | 17:00 | Jose | 12 | 9.29 | 1.24 | 0.42 |  | 10 | 4.1 | 4.66 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-11 | 5pm | 17:00 | Victor | 12 | 7.6 | 0.79 | 0.81 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | FALSE
San Juan Planes | 2025-12-15 | 3am | 03:00 | Victor | 12 | 38.62 | 1.3 | 0.7 |  | 40 | 16 | 15 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142338.jpg | TRUE | record_time / turbidity_raw_ntu unclear
San Juan Planes | 2025-12-15 | 5am | 05:00 | Victor | 12 | 37.1 | 1.93 | 0.77 |  | 40 | 16 | 15 |  | 35 | 0.7 | 0.3 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-15 | 7pm | 19:00 | Victor | 12 | 41.06 | 1.79 | 1.16 |  | 40 | 16 | 15 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-15 | 9pm | 21:00 | Victor | 12 | 33.4 | 0.89 | 0.68 |  | 40 | 16 | 15 |  | 50 | 0.6 | 0.5 |  |  |  | 20260107_142338.jpg | TRUE | chlorine_slider_pct: 50 or 30?
San Juan Planes | 2025-12-15 | 11pm | 23:00 | Victor | 12 | 37.39 | 1.15 | 0.5 |  | 40 | 18 | 15 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-16 | 7:00 | 07:00 | Tulio | 12 | 34.45 | 1.51 | 0.68 |  | 40 | 16 | 12 |  | 35 | 0.7 | 0.3 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-16 | 7:00 | 07:00 | Jose | 12 | 20.42 | 1.7 | 0.72 |  | 30 | 12.3 | 11.3 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-16 | 9:00 | 09:00 | Tulio | 12 | 38.13 | 1.2 | 0.56 |  | 40 | 16 | 12 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | TRUE | turbidity_raw_ntu 38.13 or 38.43?
San Juan Planes | 2025-12-16 | 9:00 | 09:00 | Jose | 12 | 20.57 | 1.58 | 0.57 |  | 30 | 12.3 | 11.3 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-16 | 11:00 | 11:00 | Tulio | 12 | 18.8 | 1.9 | 0.77 |  | 30 | 12.3 | 12 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-16 | 11:00 | 11:00 | Jose | 12 | 18.55 | 1.2 | 0.63 |  | 30 | 12.3 | 11.3 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-16 | 1:00 | 13:00 | Tulio | 12 | 19.5 | 1.16 | 0.78 |  | 30 | 12.3 | 12 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-16 | 3:00 | 15:00 | Tulio | 12 | 21.1 | 1.09 | 0.85 |  | 30 | 12.3 | 12 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-16 | 5:00 | 17:00 | Tulio | 12 | 21.46 | 3.51 | 1.69 |  | 30 | 12.3 | 12 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-17 | 7am | 07:00 | Victor | 12 | 16.07 | 1.24 | 0.98 |  | 30 | 12.3 | 11 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-17 | 9am | 09:00 | Victor | 12 | 15.74 | 0.64 | 0.33 |  | 20 | 8.2 | 10 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142338.jpg | TRUE | time written 7am again; likely 9am
San Juan Planes | 2025-12-17 | 11am | 11:00 | Victor | 12 | 12.95 | 1.11 | 0.34 |  | 20 | 8.2 | 10 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-17 | 1:00 | 13:00 | Jose | 12 | 17.4 | 1.17 | 0.54 |  | 30 | 12.3 | 11.3 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | TRUE | turbidity_raw_ntu unclear
San Juan Planes | 2025-12-17 | 1pm | 13:00 | Victor | 12 | 14.3 | 0.42 | 0.41 |  | 20 | 8.2 | 10 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-17 | 3:00 | 15:00 | Jose | 12 | 16.57 | 1.34 | 0.73 |  | 30 | 12.3 | 11.3 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-17 | 3pm | 15:00 | Victor | 12 | 15.91 | 1.46 | 0.5 |  | 20 | 8.2 | 10 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-17 | 5:00 | 17:00 | Jose | 12 | 15.38 | 1.68 | 1.59 |  | 30 | 12.3 | 11.3 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-17 | 5pm | 17:00 | Victor | 12 | 15.37 | 0.72 | 0.44 |  | 20 | 8.2 | 10 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142338.jpg | FALSE
San Juan Planes | 2025-12-28 | 7:00 | 07:00 | Jose | 12 | 10.92 | 1.5 | 0.88 |  | 20 | 8.2 | 8.3 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-28 | 9:00 | 09:00 | Jose | 12 | 11.03 | 1.38 | 0.7 |  | 20 | 8.2 | 8 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-28 | 11:00 | 11:00 | Jose | 12 | 5 | 1.68 | 1.08 |  | 20 | 8.2 | 8 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142343.jpg | TRUE | turbidity_raw_ntu unclear
San Juan Planes | 2025-12-28 | 11:30 | 11:30 | Tulio | 12 | 13.43 | 3.03 | 0.86 |  | 20 | 8.2 | 8.3 |  | 20 | 0.44 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-28 | 1:00 | 13:00 | Tulio | 12 | 12.31 | 1.91 | 0.86 |  | 20 | 8.2 | 8.3 |  | 20 | 0.44 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-28 | 3:00 | 15:00 | Tulio | 12 | 6.08 | 1.53 | 0.8 |  | 20 | 8.2 | 8.3 |  | 20 | 0.44 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-28 | 5:00 | 17:00 | Tulio | 12 | 8.39 | 1.76 | 0.75 |  | 20 | 8.2 | 8.3 |  | 20 | 0.44 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-29 | 7am | 07:00 | Victor | 12 | 7.49 | 1.07 | 0.76 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-29 | 7:00 | 07:00 | Tulio | 12 | 7.61 | 1.86 | 0.98 |  | 20 | 8.2 | 8.3 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-29 | 9am | 09:00 | Victor | 12 | 9.66 | 1.97 | 0.88 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-29 | 9:00 | 09:00 | Tulio | 12 | 8.93 | 1.32 | 0.93 |  | 20 | 8.2 | 8.3 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-29 | 11am | 11:00 | Victor | 12 | 5.29 | 1.67 | 0.69 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-29 | 11:00 | 11:00 | Tulio | 12 | 7.43 | 1.65 | 0.8 |  | 20 | 8.2 | 8.3 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-29 | 1:00 | 13:00 | Jose | 12 | 7 | 1.65 | 1.07 |  | 20 | 8.2 | 8 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142343.jpg | TRUE | turbidity_raw_ntu unclear
San Juan Planes | 2025-12-29 | 1pm | 13:00 | Victor | 12 | 4.16 | 0.95 | 0.39 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-29 | 3:00 | 15:00 | Jose | 12 | 9.08 | 1.17 | 0.74 |  | 20 | 8.2 | 8 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-29 | 3pm | 15:00 | Victor | 12 | 7.2 | 1.19 | 0.88 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-29 | 5:00 | 17:00 | Jose | 12 | 7.66 | 1.17 | 0.68 |  | 20 | 8.2 | 8 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-29 | 5pm | 17:00 | Victor | 12 | 8.52 | 1.3 | 0.46 |  | 10 | 4.1 | 4.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-30 | 1am | 01:00 | Victor | 12 | 15.22 | 1.33 | 0.76 |  | 20 | 8.2 | 7 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-30 | 7:00 | 07:00 | Jose | 12 | 28.57 | 1.09 | 0.85 |  | 20 | 8.2 | 7.66 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142343.jpg | TRUE | turbidity_raw_ntu 28.57?
San Juan Planes | 2025-12-30 | 9:00 | 09:00 | Jose | 12 | 26.76 | 1.23 | 0.94 |  | 20 | 8.2 | 7.66 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-30 | 11:00 | 11:00 | Jose | 12 | 25.36 | 1.74 | 1.13 |  | 20 | 8.2 | 7.66 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-30 | 1:00 | 13:00 | Tulio | 12 | 7.89 | 1.35 | 0.8 |  | 20 | 8.2 | 8.3 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-30 | 1:00 | 13:00 | Jose | 12 | 15.61 | 1.24 | 0.91 |  | 20 | 8.2 | 7.66 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142333.jpg | TRUE | chlorine_dose_probeta written '4'?
San Juan Planes | 2025-12-30 | 3:00 | 15:00 | Tulio | 12 | 11.19 | 1.2 | 0.82 |  | 20 | 8.2 | 8.3 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-30 | 3:00 | 15:00 | Jose | 12 | 22.26 | 1.53 | 0.98 |  | 20 | 8.2 | 7.66 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142333.jpg | TRUE | chlorine_dose_probeta written '4'?
San Juan Planes | 2025-12-30 | 5:00 | 17:00 | Tulio | 12 | 7.6 | 1.48 | 0.81 |  | 20 | 8.2 | 8.3 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142343.jpg | FALSE
San Juan Planes | 2025-12-30 | 5:00 | 17:00 | Jose | 12 | 21.27 | 1.4 | 0.94 |  | 20 | 8.2 | 7 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-30 | 7pm | 19:00 | Victor | 12 | 18.76 | 1.05 | 0.85 |  | 20 | 8.2 | 7 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-30 | 9pm | 21:00 | Victor | 12 | 15.51 | 1.24 | 0.98 |  | 20 | 8.2 | 7 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-30 | 11pm | 23:00 | Victor | 12 | 15.57 | 1.85 | 0.71 |  | 20 | 8.2 | 7 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-31 | 5am | 05:00 | Victor | 12 | 14.2 | 1.04 | 0.85 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-31 | 7:00 | 07:00 | Tulio | 12 | 15.94 | 1.74 | 0.99 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-31 | 7:00 | 07:00 | Jose | 12 | 8.51 | 1.21 | 1.07 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-31 | 9:00 | 09:00 | Tulio | 12 | 17.28 | 1.28 | 0.84 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-31 | 9:00 | 09:00 | Jose | 12 | 7.53 | 1.41 | 1.12 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-31 | 11:00 | 11:00 | Tulio | 12 | 4.65 | 1.29 | 0.85 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-31 | 11:00 | 11:00 | Jose | 12 | 3.68 | 1.5 | 1.27 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-31 | 1:00 | 13:00 | Tulio | 12 | 7.15 | 1.3 | 0.97 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-31 | 3:00 | 15:00 | Tulio | 12 | 5.87 | 1.16 | 0.98 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2025-12-31 | 5:00 | 17:00 | Tulio | 12 | 6.54 | 1.18 | 0.97 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2026-01-01 | 7am | 07:00 | Victor | 12 | 13.72 | 1.01 | 0.78 |  | 15 | 6.15 | 5 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2026-01-01 | 7:00 | 07:00 | Tulio | 12 | 13.6 | 1.31 | 0.84 |  | 10 | 4.1 | 5 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-01 | 9am | 09:00 | Victor | 12 | 16.36 | 1.04 | 1.06 |  | 15 | 6.15 | 5 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2026-01-01 | 9:00 | 09:00 | Tulio | 12 | 7.45 | 1.28 | 1.9 |  | 10 | 4.1 | 5 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | TRUE | turbidity_filtered 1.9?
San Juan Planes | 2026-01-01 | 11am | 11:00 | Victor | 12 | 10.66 | 1.45 | 0.97 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2026-01-01 | 11:00 | 11:00 | Tulio | 12 | 8.82 | 1.34 | 0.96 |  | 10 | 4.1 | 5 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-01 | 1pm | 13:00 | Victor | 12 | 9.18 | 1.31 | 0.85 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2026-01-01 | 3:00 | 15:00 | Jose | 12 | 15.26 | 1.57 | 0.91 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | TRUE | time circled/unclear
San Juan Planes | 2026-01-01 | 3pm | 15:00 | Victor | 12 | 8.5 | 1.46 | 0.52 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2026-01-01 | 5pm | 17:00 | Victor | 12 | 11.33 | 0.82 | 0.66 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | FALSE
San Juan Planes | 2026-01-01 |  |  |  |  | 20.76 | 1.53 | 1.54 |  | 15 | 6.15 | 5 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | TRUE | partial/transition row; date,time,operator blank
San Juan Planes | 2026-01-02 | 1am | 01:00 | Victor | 12 | 9.85 | 1.5 | 0.51 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 5am | 05:00 | Victor | 12 | 8.72 | 1.8 | 0.46 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 7:00 | 07:00 | Jose | 12 | 13.35 | 2.15 | 0.96 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 9:00 | 09:00 | Jose | 12 | 11.12 | 1.35 | 0.86 |  | 10 | 4.1 | 3.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 11:00 | 11:00 | Jose | 12 | 9.39 | 1.49 | 0.94 |  | 10 | 4.1 | 3.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 1:00 | 13:00 | Tulio | 12 | 6.78 | 1.24 | 0.88 |  | 10 | 4.1 | 5 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 1:00 | 13:00 | Jose | 12 | 8.13 | 1.96 | 0.81 |  | 10 | 4.1 | 3.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 3:00 | 15:00 | Tulio | 12 | 11.03 | 1.38 | 0.88 |  | 10 | 4.1 | 5 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 3:00 | 15:00 | Jose | 12 | 10.56 | 1.69 | 0.54 |  | 10 | 4.1 | 3.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 5:00 | 17:00 | Tulio | 12 | 11.2 | 1.31 | 0.94 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 5:00 | 17:00 | Jose | 12 | 11.91 | 1.98 | 0.9 |  | 10 | 4.1 | 3.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 7pm | 19:00 | Victor | 12 | 7.06 | 1.37 | 0.71 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 9pm | 21:00 | Victor | 12 | 8.97 | 1.32 | 0.61 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-02 | 11pm | 23:00 | Victor | 12 | 10.91 | 0.98 | 0.21 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-03 | 7:00 | 07:00 | Tulio | 11 | 10.19 | 1.29 | 0.89 |  | 15 | 4.1 | 5.8 |  | 26 | 0.5 | 0.5 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-03 | 7:00 | 07:00 | Jose | 11 | 8.49 | 1.58 | 0.91 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-03 | 9:00 | 09:00 | Tulio | 11 | 11.37 | 1.41 | 0.84 |  | 15 | 4.1 | 5.8 |  | 26 | 0.5 | 0.5 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-03 | 9:00 | 09:00 | Jose | 11 | 11.03 | 1.31 | 0.89 |  | 10 | 4.1 | 4.03 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-03 | 11:00 | 11:00 | Tulio | 11 | 4.01 | 1.48 | 0.96 |  | 15 | 4.1 | 5.8 |  | 26 | 0.5 | 0.5 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-03 | 1:00 | 13:00 | Tulio | 11 | 6.17 | 1.44 | 0.81 |  | 15 | 4.1 | 5.8 |  | 26 | 0.5 | 0.5 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-03 | 1:00 | 13:00 | Jose | 11 | 8.3 | 1.61 | 0.9 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142319.jpg | TRUE | time unclear (1:00?)
San Juan Planes | 2026-01-03 | 3:00 | 15:00 | Tulio | 11 | 8.74 | 1.54 | 0.86 |  | 15 | 4.1 | 5.8 |  | 26 | 0.5 | 0.5 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-03 | 3:00 | 15:00 | Jose | 11 | 8.35 | 1.44 | 0.84 |  | 10 | 4.1 | 6.34 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142319.jpg | TRUE | coag_dose_probeta unclear
San Juan Planes | 2026-01-03 | 5:00 | 17:00 | Tulio | 11 | 7.65 | 1.18 | 0.99 |  | 15 | 4.1 | 5.8 |  | 26 | 0.5 | 0.5 |  |  |  | 20260107_142324.jpg | FALSE
San Juan Planes | 2026-01-03 | 5:00 | 17:00 | Jose | 11 | 8.64 | 1.4 | 0.88 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 7am | 07:00 | Victor | 12 | 7.8 | 1.73 | 0.99 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 7:00 | 07:00 | Tulio | 12 | 7.27 | 1.3 | 0.91 |  | 20 | 8.2 | 8.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 9am | 09:00 | Victor | 12 | 7.61 | 1.63 | 0.75 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 9:00 | 09:00 | Tulio | 12 | 7.13 | 1.27 | 0.44 |  | 20 | 8.2 | 8.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 11am | 11:00 | Victor | 12 | 9.23 | 1.27 | 0.72 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 11:00 | 11:00 | Tulio | 12 | 8.27 | 1.35 | 0.9 |  | 20 | 8.2 | 8.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 1pm | 13:00 | Victor | 12 | 7.04 | 1.31 | 0.81 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 1:00 | 13:00 | Tulio | 12 | 9.6 | 1.16 | 0.82 |  | 20 | 8.2 | 8.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 3pm | 15:00 | Victor | 12 | 8.44 | 1.37 | 0.9 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 3:00 | 15:00 | Tulio | 12 | 16.37 | 1.31 | 1.01 |  | 20 | 8.2 | 8.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 5pm | 17:00 | Victor | 12 | 8.76 | 1.3 | 0.84 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-04 | 5:00 | 17:00 | Tulio | 12 | 8.9 | 0.79 | 0.83 |  | 20 | 8.2 | 8.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-05 | 7:00 | 07:00 | Jose | 12 | 9.45 | 1.72 | 0.65 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-05 | 9:00 | 09:00 | Jose | 12 | 6.68 | 1.29 | 0.68 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-05 | 11:00 | 11:00 | Jose | 12 | 9.51 | 1.61 | 0.85 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-05 | 1:00 | 13:00 | Jose | 12 | 9.46 | 1.53 | 0.97 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-05 | 3:00 | 15:00 | Jose | 12 | 5.98 | 1.5 | 0.97 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-05 | 5:00 | 17:00 | Jose | 12 | 8.77 | 1.8 | 0.87 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142319.jpg | FALSE
San Juan Planes | 2026-01-05 | 7pm | 19:00 | Victor | 12 | 8.86 | 1.4 | 0.64 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-05 | 9pm | 21:00 | Victor | 12 | 9.07 | 1.09 | 0.71 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | TRUE | turbidity_raw unclear
San Juan Planes | 2026-01-05 | 11pm | 23:00 | Victor | 12 | 9.01 | 1.76 | 0.64 |  | 10 | 4.1 | 4.3 |  | 50 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | TRUE | chlorine_slider 50 or 30?
San Juan Planes | 2026-01-06 | 1am | 01:00 | Victor | 12 | 9.12 | 1.8 | 0.72 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-06 | 5am | 05:00 | Victor | 12 | 11.16 | 1.35 | 0.81 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-06 | 7:00 | 07:00 | Tulio | 12 | 9.88 | 1.77 | 0.94 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-06 | 7:00 | 07:00 | Jose | 11 | 10.32 | 1.09 | 0.84 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-06 | 9:00 | 09:00 | Tulio | 12 | 8.77 | 1.95 | 0.86 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-06 | 9:00 | 09:00 | Jose | 11 | 9.7 | 1.46 | 1 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-06 | 11:00 | 11:00 | Tulio | 12 | 5.21 | 1.48 | 0.97 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-06 | 11:00 | 11:00 | Jose | 11 | 9.58 | 1.06 | 1.13 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-06 | 1:00 | 13:00 | Tulio | 11.5 | 6.25 | 1.97 | 1.16 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-06 | 3:00 | 15:00 | Tulio | 11.5 | 4.39 | 0.96 | 0.64 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-06 | 5:00 | 17:00 | Tulio | 11 | 6.87 | 1.39 | 0.73 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-07 | 7am | 07:00 | Victor | 12 | 8.87 | 0.93 | 0.92 |  | 15 | 6.15 | 5 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-07 | 9am | 09:00 | Victor | 12 | 7.44 | 0.98 | 0.48 |  | 15 | 6.15 | 5 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-07 | 11am | 11:00 | Victor | 12 | 8.86 | 0.97 | 0.63 |  | 100 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | TRUE | coag_slider 100? likely 10
San Juan Planes | 2026-01-07 | 1pm | 13:00 | Victor | 12 | 8.86 | 0.97 | 0.05 |  | 10 | 4.1 | 4.3 |  | 50 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | TRUE | chlorine_slider 50 or 30?
San Juan Planes | 2026-01-07 | 3:00 | 15:00 | Jose | 11 | 9.46 | 1.26 | 0.48 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | TRUE | time unclear
San Juan Planes | 2026-01-07 | 3pm | 15:00 | Victor | 12 | [14 empty] | 20260107_142308.jpg | TRUE | row blank except caudal
San Juan Planes | 2026-01-07 | 5:00 | 17:00 | Jose | 11 | 7.26 | 1.24 | 0.95 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | FALSE
San Juan Planes | 2026-01-07 | 5pm | 17:00 | Victor | 12 | [14 empty] | 20260107_142308.jpg | TRUE | row blank except caudal

## REVIEW_QUEUE
plant | record_date | record_time | record_time_24h | operator | flow_lps | turbidity_raw_ntu | turbidity_clarified_ntu | turbidity_filtered_ntu | coag_num_hoses | coag_slider_pct | coag_dose_pct_mgl | coag_dose_probeta_mgl | coag_tank_vol_l | chlorine_slider_pct | chlorine_dose_pct_mgl | chlorine_dose_probeta_mgl | chlorine_tank_vol_l | has_flocs | purge | source_image | needs_review | review_notes
San Juan Planes | 2025-07-26 | 7 | 07:00 | Silvia | 11 | 2.02 | 0.31 |  | 3 | 12 | 2.12 | 5.45 | 210 | 28 | 0.5 | 0.5 | 90 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X' (no reading)
San Juan Planes | 2025-07-26 | 8:00 | 08:00 | Jose | 11 | 1.52 | 4.45 | 2.58 | 7 | 36 | 6.37 | 16 | 190 | 30 | 0.6 | 0.3 | 60 |  |  | 20260107_143129.jpg | TRUE | coag block values very unclear
San Juan Planes | 2025-07-26 | 8:30 | 08:30 | Jose | 11 | 2.47 | 0.36 |  | 7 | 62 | 1.09 | 28 | 190 | 30 | 0.6 | 0.3 | 60 |  |  | 20260107_143129.jpg | TRUE | coag block values very unclear
San Juan Planes | 2025-07-26 | 9 | 09:00 | Silvia | 10.5 | 1.46 | 0.4 |  | 3 | 10 | 1.77 | 4.95 | 200 | 30 | 0.6 | 0.5 | 80 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X'
San Juan Planes | 2025-07-26 | 9:00 | 09:00 | Jose | 11 | 1.27 | 1.44 | 0.1 | 7 | 30 | 5.36 | 14 | 196 | 36 | 0.6 | 0.3 | 60 |  |  | 20260107_143129.jpg | TRUE | coag block values unclear
San Juan Planes | 2025-07-26 | 11 | 11:00 | Silvia | 10.5 | 1.91 | 0.89 |  | 3 | 10 | 1.77 | 4.57 | 195 | 30 | 0.6 | 0.4 | 70 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X'
San Juan Planes | 2025-07-26 | 11:00 | 11:00 | Jose | 11 | 7.34 | 0.82 | 0.09 | 3 | 30 | 5.31 | 13 | 190 | 30 | 0.6 | 0.3 | 60 |  |  | 20260107_143129.jpg | TRUE | coag block unclear
San Juan Planes | 2025-07-26 | 1:30 | 13:30 | Silvia | 10.5 | 1.53 | 0.3 |  | 3 | 10 | 1.77 | 4.95 | 190 | 30 | 0.6 | 0.4 | 65 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X'
San Juan Planes | 2025-07-26 | 3:30 | 15:30 | Silvia | 12 | 10.61 | 0.63 |  | 3 | 10 | 1.77 | 4.33 | 185 | 30 | 0.6 | 0.4 | 60 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X'; raw unclear
San Juan Planes | 2025-07-26 | 5:20 | 17:20 | Silvia | 11 | 2.04 | 0.96 |  | 7 | 10 | 1.77 | 5.45 | 180 | 30 | 0.6 | 0.4 | 60 |  |  | 20260107_143129.jpg | TRUE | filtrada 'X'
San Juan Planes | 2025-07-27 | 2:00 | 14:00 | Jose | 11 | 4.88 | 0.69 | 0 | 3 | 30 | 5.31 | 9.4 | 150 | 30 | 0.8 | 0.2 | 50 |  |  | 20260107_143129.jpg | TRUE | coag block unclear
San Juan Planes | 2025-07-29 | 7:00 | 07:00 | Jose | 10.5 | 1.96 | 1.1 | 0.01 | 7 | 6 | 2.46 | 2.46 | 360 | 25 | 0.5 | 0.5 | 100 |  |  | 20260107_143120.jpg / _143121.jpg / _143123.jpg (same page) | TRUE | coag block partly unclear
San Juan Planes | 2025-07-31 | 7am | 07:00 | Hildeen | 10.5 | 1.89 | 0.41 | 0 | 7 | 7 | 2.87 | 2.85 | 400 | 30 | 0.6 | 0.6 | 100 |  |  | 20260107_143113.jpg | TRUE | operator name spelling
San Juan Planes | 2025-07-31 | 1pm | 13:00 | Hildeen | 10 | 1.93 | 0.22 | 0 | 7 | 7 | 2.87 | 3.6 | 398 | 30 | 0.6 | 0.5 | 70 |  |  | 20260107_143113.jpg | TRUE | coag probeta 3.6?
San Juan Planes | 2025-08-01 | 11:00 | 11:00 | Jose | 10.5 | 2.53 | 0.66 | 0 | 7 | 7 | 2.87 | 2.87 | 420 | 50 | 0.1 | 0.4 | 36 |  |  | 20260107_143104.jpg | TRUE | coag probeta overwritten
San Juan Planes | 2025-12-09 | 9pm | 21:00 | Victor | 12 | 6.92 | 0.52 | 0.74 |  | 10 | 4.1 | 4 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142313.jpg | TRUE | turbidity_raw_ntu 6.92?
San Juan Planes | 2025-12-10 | 7:00 | 07:00 | Jose | 12 | 6.17 | 0.85 | 0.58 |  | 10 | 4.1 | 4.66 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142313.jpg | TRUE | chlorine_dose_probeta unclear
San Juan Planes | 2025-12-11 | 3:00 | 15:00 | Jose | 12 | 8.86 | 0.76 | 0.78 |  | 10 | 4.1 | 4.66 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142313.jpg | TRUE | turbidity_clarified unclear
San Juan Planes | 2025-12-15 | 3am | 03:00 | Victor | 12 | 38.62 | 1.3 | 0.7 |  | 40 | 16 | 15 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142338.jpg | TRUE | record_time / turbidity_raw_ntu unclear
San Juan Planes | 2025-12-15 | 9pm | 21:00 | Victor | 12 | 33.4 | 0.89 | 0.68 |  | 40 | 16 | 15 |  | 50 | 0.6 | 0.5 |  |  |  | 20260107_142338.jpg | TRUE | chlorine_slider_pct: 50 or 30?
San Juan Planes | 2025-12-16 | 9:00 | 09:00 | Tulio | 12 | 38.13 | 1.2 | 0.56 |  | 40 | 16 | 12 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | TRUE | turbidity_raw_ntu 38.13 or 38.43?
San Juan Planes | 2025-12-17 | 9am | 09:00 | Victor | 12 | 15.74 | 0.64 | 0.33 |  | 20 | 8.2 | 10 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142338.jpg | TRUE | time written 7am again; likely 9am
San Juan Planes | 2025-12-17 | 1:00 | 13:00 | Jose | 12 | 17.4 | 1.17 | 0.54 |  | 30 | 12.3 | 11.3 |  | 30 | 0.6 | 0.3 |  |  |  | 20260107_142338.jpg | TRUE | turbidity_raw_ntu unclear
San Juan Planes | 2025-12-28 | 11:00 | 11:00 | Jose | 12 | 5 | 1.68 | 1.08 |  | 20 | 8.2 | 8 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142343.jpg | TRUE | turbidity_raw_ntu unclear
San Juan Planes | 2025-12-29 | 1:00 | 13:00 | Jose | 12 | 7 | 1.65 | 1.07 |  | 20 | 8.2 | 8 |  | 20 | 0.4 | 0.5 |  |  |  | 20260107_142343.jpg | TRUE | turbidity_raw_ntu unclear
San Juan Planes | 2025-12-30 | 7:00 | 07:00 | Jose | 12 | 28.57 | 1.09 | 0.85 |  | 20 | 8.2 | 7.66 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142343.jpg | TRUE | turbidity_raw_ntu 28.57?
San Juan Planes | 2025-12-30 | 1:00 | 13:00 | Jose | 12 | 15.61 | 1.24 | 0.91 |  | 20 | 8.2 | 7.66 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142333.jpg | TRUE | chlorine_dose_probeta written '4'?
San Juan Planes | 2025-12-30 | 3:00 | 15:00 | Jose | 12 | 22.26 | 1.53 | 0.98 |  | 20 | 8.2 | 7.66 |  | 35 | 0.7 | 0.4 |  |  |  | 20260107_142333.jpg | TRUE | chlorine_dose_probeta written '4'?
San Juan Planes | 2026-01-01 | 9:00 | 09:00 | Tulio | 12 | 7.45 | 1.28 | 1.9 |  | 10 | 4.1 | 5 |  | 30 | 0.6 | 0.4 |  |  |  | 20260107_142324.jpg | TRUE | turbidity_filtered 1.9?
San Juan Planes | 2026-01-01 | 3:00 | 15:00 | Jose | 12 | 15.26 | 1.57 | 0.91 |  | 20 | 8.2 | 8 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | TRUE | time circled/unclear
San Juan Planes | 2026-01-01 |  |  |  |  | 20.76 | 1.53 | 1.54 |  | 15 | 6.15 | 5 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142333.jpg | TRUE | partial/transition row; date,time,operator blank
San Juan Planes | 2026-01-03 | 1:00 | 13:00 | Jose | 11 | 8.3 | 1.61 | 0.9 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142319.jpg | TRUE | time unclear (1:00?)
San Juan Planes | 2026-01-03 | 3:00 | 15:00 | Jose | 11 | 8.35 | 1.44 | 0.84 |  | 10 | 4.1 | 6.34 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142319.jpg | TRUE | coag_dose_probeta unclear
San Juan Planes | 2026-01-05 | 9pm | 21:00 | Victor | 12 | 9.07 | 1.09 | 0.71 |  | 10 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | TRUE | turbidity_raw unclear
San Juan Planes | 2026-01-05 | 11pm | 23:00 | Victor | 12 | 9.01 | 1.76 | 0.64 |  | 10 | 4.1 | 4.3 |  | 50 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | TRUE | chlorine_slider 50 or 30?
San Juan Planes | 2026-01-07 | 11am | 11:00 | Victor | 12 | 8.86 | 0.97 | 0.63 |  | 100 | 4.1 | 4.3 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | TRUE | coag_slider 100? likely 10
San Juan Planes | 2026-01-07 | 1pm | 13:00 | Victor | 12 | 8.86 | 0.97 | 0.05 |  | 10 | 4.1 | 4.3 |  | 50 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | TRUE | chlorine_slider 50 or 30?
San Juan Planes | 2026-01-07 | 3:00 | 15:00 | Jose | 11 | 9.46 | 1.26 | 0.48 |  | 15 | 6.15 | 5.6 |  | 30 | 0.6 | 0.5 |  |  |  | 20260107_142308.jpg | TRUE | time unclear
San Juan Planes | 2026-01-07 | 3pm | 15:00 | Victor | 12 | [14 empty] | 20260107_142308.jpg | TRUE | row blank except caudal
San Juan Planes | 2026-01-07 | 5pm | 17:00 | Victor | 12 | [14 empty] | 20260107_142308.jpg | TRUE | row blank except caudal